## Final Design
FINAL DESIGN – 33 kV substation grounding grid (30 × 30 m yard), CYMGRD 6.3 / IEEE Std 80
Design description
Grid | 6 × 6 bare annealed Cu conductors, 70 mm² (9.44 mm), 6 m mesh, 0.5 m depth, 0–30 m
Perimeter ring | 32 × 32 m ring 1 m outside the fence (−1 to 31 m), 6 elements/side, tied to all 24 grid-line ends
Ground rods | 20 × 16 mm Cu-bonded steel, 9 m (3 × 3 m sections) on the ring – corners + every 6 m
Joints | Exothermic welds at all crossings, ties and rod connections
Fence | On the 30 × 30 m line, bonded to the grid; gate swings inward
Surface layer | 0.1 m wet crushed rock (2500 Ω·m), extended ≥1.5 m outside the fence
Fault basis | 13,110 A LG at B1 (33 kV), X/R 45, t = 0.5 s, split factor 0.276, decrement 1.134
Safety verification
Check | Worst value (V) | Limit (V) | Margin | Result | Source
Touch – inside the grid | 666.36 | 806.59 | 17.39% | PASS | Profile (−1,−1)→(31,31)
Touch – 1 m outside the fence | 609.74 | 806.59 | 24.41% | PASS | Profile (−1,−1)→(31,−1)
Step – everywhere (to 6 m outside) | 149.07 | 2560.25 | 94.18% | PASS | Profile (−6,−6)→(36,36)
Overall result |  |  |  | PASS
Governing margin (lowest touch margin) |  |  | 17.39%
GPR (V) | 2635.21
Split factor used / max split factor before touch limit is reached | 0.27589 | 0.33395 |  |  | Touch scales linearly with grid current, so the design stays safe while Sf is below this value
Cost (Bangladesh market, Sep-2026)
Installed grid + ring + rods + joints (direct) | 1541517.9366
TOTAL budget incl. crushed rock, tests, OH&P, contingency, VAT (BDT) | 3334519.8027
TOTAL budget (lakh BDT) | 33.3452
TOTAL budget (USD) | 27131.9756
Grid-only budget incl. mark-ups (excl. crushed rock) | 2131620.3737
Typical earthing budget range – low | 500000
Typical earthing budget range – high | 2000000
Grid-only budget vs typical range | Above range
Full budget vs typical range | Above range
Why 6×6 + ring over the cheaper 5×5 + ring
Item | 6×6 + ring (FINAL) | 5×5 + ring | Difference
Touch inside (V) | 666.36 | 722.395 | -56.035
Touch margin inside | 17.39% | 10.44% | 6.947%
Touch at fence (V) | 609.74 | 612.575 | -2.835
Max tolerable split factor | 0.33395 | 0.30804 | 0.025904
Total budget (BDT) | 3334519.8027 | 3145598.006 | 188921.7967
Decision | 6×6 + ring gives ~7 percentage points more touch margin inside the grid and tolerates a higher split factor, for about 6% (≈৳1.9 lakh) more total budget. Both perform alike at the fence (the ring governs there). Unverified inputs (soil model, split factor) justify the larger margin.
Design history
Stage | Design | Touch inside (V) | Touch at fence (V) | Outcome
1 – Parametric sweep | 6×6, 20 rods × 9 m (best of sweeps A–C) | 714.443 | Not checked | Passed inside; mesh/rod options ranked by cost
2 – Perimeter check | Same, contour (−5,−5)→(35,35) | 714.443 | > 806.59 (contour) | FAILED outside the fence → perimeter ring added
3 – Ring added | 6×6 + ring (1 element/side) | 669.213 | 631.453 | Passed; ring segmentation refined
4 – Verification | 6×6 + ring (6 elements/side) | 666.36 | 609.74 | PASS – FINAL
4 – Alternative | 5×5 + ring (6 elements/side) | 722.395 | 612.575 | PASS, thin margin – rejected
Construction notes: fence on the 0–30 m line bonded to grid · crushed rock ≥1.5 m outside fence · gate swings inward · no grid-bonded metal outside the ring.
Accessible zone: touch evaluated inside the fence and 1 m outside it (IEEE 80 reach); step evaluated everywhere. Contour maxima 5 m outside (≈1400 V) are not accessible.
Assumptions to state: two-layer soil 100/50 Ω·m (1.5 m) · split factor 0.276 · X/R 45 (conservative vs ≈24 from fault angle) · 70 kg body, 0.5 s.
Costs are indicative Dhaka-market estimates (see 'Unit Rates'); confirm yellow-highlighted rates with supplier quotations.

## Sweep A
#Run | Grid spacing (X×Y) | # Rods | Rod length(m) | Total conductor length (m) | Total rod length (m) | Ground Resistance (Ω) | GPR (V) | Touch (V) | Step (V) | Pass/Fail | Est. material cost | Conductors per direction (n) | Conductor length (m) | Rod length (m) | Exothermic joints (n² + rods) | Rod couplers | Conductor cost (BDT) | Rod cost (BDT) – whole 3 m sections | Joint cost (BDT) | Touch margin vs limit | Est. cost (USD)
1 | 4x4 | 20 | 9 | 2*4*30 | 20*9 | 0.67004 | 2694 | 887.516 | 163.9 | FAIL | 977774.0328 | 4 | 240 | 180 | 36 | 40 | 419774.0328 | 486000 | 72000 | -10.03% | 7955.8506
2 | 4x4 asymmetric | 20 | 9 | 2*4*30 | 20*9 | - | - | 856.141 | 152.5 | FAIL | 977774.0328 | 4 | 240 | 180 | 36 | 40 | 419774.0328 | 486000 | 72000 | -6.143% | 7955.8506
3 | 5x5 | 20 | 9 | 2*5*30 | 20*9 | 0.66186 | 2685.03 | 751.441 | 128.89 | PASS | 1100717.541 | 5 | 300 | 180 | 45 | 40 | 524717.541 | 486000 | 90000 | 6.837% | 8956.2046
4 | 6x6 | 20 | 9 | 2*6*30 | 20*9 | 0.65184 | 2673.81 | 714.443 | 111.88 | PASS | 1227661.0492 | 6 | 360 | 180 | 56 | 40 | 629661.0492 | 486000 | 112000 | 11.42% | 9989.1054
5 | 8x8 | 20 | 9 | 2*8*30 | 20*9 | 0.64413 | 2665.02 | 654.096 | 99.48 | PASS | 1493548.0656 | 8 | 480 | 180 | 84 | 40 | 839548.0656 | 486000 | 168000 | 18.91% | 12152.5473
6 | 10x10 | 20 | 9 | 2*10*30 | 20*9 | 0.6418 | 2662.32 | 634.313 | 99.38 | PASS | 1775435.082 | 10 | 600 | 180 | 120 | 40 | 1049435.082 | 486000 | 240000 | 21.36% | 14446.1764
Cost columns L and M–V added: formulas use rates on the 'Unit Rates' sheet. Negative touch margin = design exceeds the tolerable touch voltage.
Note on L1: Installed cost in BDT of grid conductor + ground rods + exothermic joints (supply + labour). Excludes surface layer, testing, mark-ups and VAT – see 'Budget vs Benchmark'. Rates on 'Unit Rates' sheet.
Note on M1: Read from column B (e.g. '5x5' = 5 conductors in each direction). Numeric copy so the cost formulas can calculate.

## Sweep B
#Run | Grid spacing (X×Y) | # Rods | Rod length(m) | Total conductor length (m) | Total rod length (m) | Ground Resistance (Ω) | GPR (V) | Touch (V) | Step (V) | Pass/Fail | Est. material cost | Conductors per direction (n) | Conductor length (m) | Rod length (m) | Exothermic joints (n² + rods) | Rod couplers | Conductor cost (BDT) | Rod cost (BDT) – whole 3 m sections | Joint cost (BDT) | Touch margin vs limit | Est. cost (USD)
1 | 5x5 | 20 | 9 | 2*5*30 | 20*9 | 0.66186 | 2685.03 | 751.441 | 128.89 | PASS | 1100717.541 | 5 | 300 | 180 | 45 | 40 | 524717.541 | 486000 | 90000 | 6.837% | 8956.2046
2 | 5x5 | 16 | 9 | 2*5*30 | 16*9 | - | - | 836.451 | 142.45 | FAIL | 995517.541 | 5 | 300 | 144 | 41 | 32 | 524717.541 | 388800 | 82000 | -3.702% | 8100.2241
3 | 5x5 | 24 | 9 | 2*5*30 | 24*9 | 0.63482 | 2654.18 | 706.932 | 118.55 | PASS | 1205917.541 | 5 | 300 | 216 | 49 | 48 | 524717.541 | 583200 | 98000 | 12.36% | 9812.185
Cost columns L and M–V added: formulas use rates on the 'Unit Rates' sheet. Negative touch margin = design exceeds the tolerable touch voltage.
Note on L1: Installed cost in BDT of grid conductor + ground rods + exothermic joints (supply + labour). Excludes surface layer, testing, mark-ups and VAT – see 'Budget vs Benchmark'. Rates on 'Unit Rates' sheet.
Note on M1: Read from column B (e.g. '5x5' = 5 conductors in each direction). Numeric copy so the cost formulas can calculate.

## Sweep c
#Run | Grid spacing (X×Y) | # Rods | Rod length(m) | Total conductor length (m) | Total rod length (m) | Ground Resistance (Ω) | GPR (V) | Touch (V) | Step (V) | Pass/Fail | Est. material cost | Conductors per direction (n) | Conductor length (m) | Rod length (m) | Exothermic joints (n² + rods) | Rod couplers | Conductor cost (BDT) | Rod cost (BDT) – whole 3 m sections | Joint cost (BDT) | Touch margin vs limit | Est. cost (USD)
1 | 5x5 | 20 | 9 | 2*5*30 | 20*9 | 0.66186 | 2685.03 | 751.441 | 128.89 | PASS | 1100717.541 | 5 | 300 | 180 | 45 | 40 | 524717.541 | 486000 | 90000 | 6.837% | 8956.2046
2 | 5x5 | 20 | 8 | 2*5*30 | 20*8 | 0.68277 | 2707.65 | 792.355 | 139.39 | PASS | 1092717.541 | 5 | 300 | 160 | 45 | 40 | 524717.541 | 478000 | 90000 | 1.765% | 8891.111
3 | 5x5 | 20 | 7 | 2*5*30 | 20*7 | - | - | 839.528 | 150.84 | FAIL | 1084717.541 | 5 | 300 | 140 | 45 | 40 | 524717.541 | 470000 | 90000 | -4.084% | 8826.0174
Cost columns L and M–V added: formulas use rates on the 'Unit Rates' sheet. Negative touch margin = design exceeds the tolerable touch voltage.
Note on L1: Installed cost in BDT of grid conductor + ground rods + exothermic joints (supply + labour). Excludes surface layer, testing, mark-ups and VAT – see 'Budget vs Benchmark'. Rates on 'Unit Rates' sheet.
Note on M1: Read from column B (e.g. '5x5' = 5 conductors in each direction). Numeric copy so the cost formulas can calculate.

## Sweep D
#Run | Grid spacing (X×Y) | # Rods | Rod length(m) | Total conductor length (m) | Total rod length (m) | Ground Resistance (Ω) | GPR (V) | Touch (V) | Step (V) | Pass/Fail | Est. material cost | Conductors per direction (n) | Conductor length (m) | Rod length (m) | Exothermic joints (n² + rods + ties) | Rod couplers | Conductor cost (BDT) | Rod cost (BDT) – whole 3 m sections | Joint cost (BDT) | Touch margin vs limit | Est. cost (USD) | Touch at fence, 1 m outside (V) | Fence touch margin | Ring elements per side | Status
1 | 6x6 + ring | 20 | 9 | grid 12×30 + ring 4×32 + 24 ties | 20*9 | - | 2635.37 | 669.213 | 141.91 | PASS | 1541517.9366 | 6 | 512 | 180 | 80 | 40 | 895517.9366 | 486000 | 160000 | 17.03% | 12542.8636 | 631.453 | 21.71% | 1 | Superseded – coarse ring model (1 element/side) overstated fence touch by ~22 V
2 | 6x6 + ring | 20 | 9 | grid 12×30 + ring 4×32 + 24 ties | 20*9 | - | 2635.21 | 666.36 | 149.07 | PASS | 1541517.9366 | 6 | 512 | 180 | 80 | 40 | 895517.9366 | 486000 | 160000 | 17.39% | 12542.8636 | 609.74 | 24.41% | 6 | FINAL DESIGN – selected
3 | 5x5 + ring | 20 | 9 | grid 10×30 + ring 4×32 + 20 ties | 20*9 | - | 2640.08 | 722.395 | 151.21 | PASS | 1399578.1946 | 5 | 448 | 180 | 65 | 40 | 783578.1946 | 486000 | 130000 | 10.44% | 11387.943 | 612.575 | 24.05% | 6 | Meets IEEE 80 but only ~10% inside margin – rejected
Stage 2 designs: 6×6 or 5×5 grid (0–30 m) + perimeter ring 32×32 m at 1 m outside the fence, tied to every grid line, 20 rods × 9 m moved onto the ring. Touch (col I) = profile (−1,−1)→(31,31); fence touch (col W) = profile (−1,−1)→(31,−1); step (col J) = max of all profiles incl. (−6,−6)→(36,36).
Pass/Fail is now a formula: touch inside AND touch at fence ≤ 806.59 V, and step ≤ 2560.25 V. Ground resistance: see CYMGRD Grid analysis report (≈ GPR / grid current).

## Unit Rates
Bangladesh unit rates & design constants (edit blue cells; yellow = key assumptions)
Item | Value | Unit | Source / basis
DESIGN CONSTANTS
Grid side length (square yard) | 30 | m | User design (CYMGRD grid 0–30 m)
Max permissible touch voltage | 806.59 | V | User CYMGRD Soil analysis report (70 kg, 0.5 s, 0.1 m wet crushed rock)
Conductor cross-section | 70 | mm² | User CYMGRD model: 9.44 mm solid Cu = 70 mm²
GRID CONDUCTOR (bare annealed Cu)
Copper density | 8.89 | g/cm³ | Physical constant (annealed Cu)
Conductor mass | 0.6223 | kg/m | Formula: area × density
Copper metal price (spot, in BDT) | 1853 | BDT/kg | commoditypriceapi.com copper→BDT, 08-Sep-2026 (৳1,853/kg)
Wire-drawing/stranding + dealer premium over metal | 30% | % | Assumption: typical 25–40% for bare stranded earthing conductor; verify with BRB/Eastern/Superior Electric quote
Conductor supply rate | 1499.0585 | BDT/m | Formula
Trench 0.5–0.6 m, lay conductor, backfill & compact | 250 | BDT/m | Assumption: local manual labour in kutcha ground; PWD SoR 2022 (2nd rev., Jan-2026) underground cable items imply ~৳200–300/m for trench+refill
GROUND RODS (16 mm Cu-bonded steel, 3 m sections)
Rod section price (16 mm × 3 m, threaded) | 6500 | BDT/each | Estimate: Superior Electric (Mirpur) lists 12.7 mm × 3 m at ৳5,000 on BDStall; 16 mm scaled for ~1.6× steel mass
Rod section length | 3 | m | Standard section length
Threaded coupler | 600 | BDT/each | Assumption
Rod driving labour (power hammer, alluvial soil) | 400 | BDT/m | Assumption
JOINTS
Exothermic weld, all-in (cartridge + mould share + labour) | 2000 | BDT/joint | Assumption: imported cartridge ≈ US$8–15 + graphite mould amortisation + labour; Indian brands (Amiable/AuraWeld) supply BD
SURFACE LAYER & SITE WORKS (same for every grid option)
Surface layer extension beyond grid edge (each side) | 1.5 | m | Final design: crushed rock ≥1.5 m outside fence (fence on grid edge) so the 806.59 V limit applies in the 1 m reach zone
Surface layer thickness | 0.1 | m | User CYMGRD model
Crushed stone (3/4") delivered | 220 | BDT/cft | BDStall stone listings Sep-2026: ৳210–230/cft
Spreading & levelling labour | 15 | BDT/cft | Assumption
Soil resistivity survey + fall-of-potential & continuity tests | 60000 | BDT lump | Assumption
MARK-UPS
Contractor overhead & profit | 10% | % | Assumption
Contingency | 10% | % | Assumption
VAT | 10% | % | PWD SoR 2022 (2nd revised, eff. 22-Jan-2026) applies VAT at 10%
Exchange rate | 122.9 | BDT/USD | Implied by commoditypriceapi.com (৳1,853/kg = US$15.08/kg), Sep-2026
BENCHMARK (typical budget)
33/11 kV substation total cost – low | 25000000 | BDT | AB Power Engineering (BD), Oct-2025: ৳2.5–4 crore for 3–10 MVA
33/11 kV substation total cost – high | 40000000 | BDT | AB Power Engineering (BD), Oct-2025
Earthing share of substation cost – low | 2% | % | Assumption (rule of thumb) – replace with a BREB/PGCB BOQ if available
Earthing share of substation cost – high | 5% | % | Assumption (rule of thumb)
STAGE 2 – PERIMETER RING & FINAL CHECKS
Ring offset outside grid edge / fence | 1 | m | User CYMGRD model: ring at −1 m and 31 m (fence on 0–30 m line)
Max permissible step voltage | 2560.25 | V | User CYMGRD Soil analysis report
Current split factor used in CYMGRD | 0.27589 | – | User CYMGRD Grid analysis report (2 lines, Rtg 15 Ω; 6 feeders, Rdg 25 Ω)
Legend: blue = input you can edit · black = formula · green = link to another sheet · yellow fill = key assumption to confirm with a local quotation.
Rates are indicative Dhaka-zone market estimates (Sep-2026) for a student design study, not a contractor quotation.

## Design Comparison
All unique designs from the sweeps – safety vs. installed grid cost
Design | Source | Grid (n×n) | Mesh spacing (m) | # Rods | Rod length (m) | Touch (V) | Step (V) | Pass/Fail | Touch margin | Installed grid cost (BDT) | Cost (USD) | Cost rank among PASS (1 = cheapest) | Extra cost vs cheapest PASS (BDT)
4×4, 20 rods × 9 m | Sweep A, run 1 | 4 | 10 | 20 | 9 | 887.516 | 163.9 | FAIL | -10.03% | 977774.0328 | 7955.8506 | – | –
4×4 asymmetric, 20 rods × 9 m | Sweep A, run 2 | 4 | 10 | 20 | 9 | 856.141 | 152.5 | FAIL | -6.143% | 977774.0328 | 7955.8506 | – | –
5×5, 20 rods × 9 m | Sweep A, run 3 | 5 | 7.5 | 20 | 9 | 751.441 | 128.89 | PASS | 6.837% | 1100717.541 | 8956.2046 | 2 | 8000
6×6, 20 rods × 9 m (Stage-1 best → final with ring, see Sweep D) | Sweep A, run 4 | 6 | 6 | 20 | 9 | 714.443 | 111.88 | PASS | 11.42% | 1227661.0492 | 9989.1054 | 4 | 134943.5082
8×8, 20 rods × 9 m | Sweep A, run 5 | 8 | 4.2857 | 20 | 9 | 654.096 | 99.48 | PASS | 18.91% | 1493548.0656 | 12152.5473 | 5 | 400830.5246
10×10, 20 rods × 9 m | Sweep A, run 6 | 10 | 3.3333 | 20 | 9 | 634.313 | 99.38 | PASS | 21.36% | 1775435.082 | 14446.1764 | 6 | 682717.541
5×5, 16 rods × 9 m | Sweep B, run 2 | 5 | 7.5 | 16 | 9 | 836.451 | 142.45 | FAIL | -3.702% | 995517.541 | 8100.2241 | – | –
5×5, 24 rods × 9 m | Sweep B, run 3 | 5 | 7.5 | 24 | 9 | 706.932 | 118.55 | PASS | 12.36% | 1205917.541 | 9812.185 | 3 | 113200
5×5, 20 rods × 8 m | Sweep c, run 2 | 5 | 7.5 | 20 | 8 | 792.355 | 139.39 | PASS | 1.765% | 1092717.541 | 8891.111 | 1 | 0
5×5, 20 rods × 7 m | Sweep c, run 3 | 5 | 7.5 | 20 | 7 | 839.528 | 150.84 | FAIL | -4.084% | 1084717.541 | 8826.0174 | – | –
[9 empty] | Cheapest PASS cost: | 1092717.541
Installed grid cost = conductor (supply + trench) + rods (sections + couplers + driving) + exothermic joints. Surface layer, testing, mark-ups & VAT are identical for all options and are handled on 'Budget vs Benchmark'.
Touch margin = (806.59 V − touch) / 806.59 V. Aim for ≥10% margin given uncertainty in split factor and soil model.
Bold row = current/recommended design. Cost ranking changes automatically if you edit the unit rates.
Stage-1 sweep only checked touch inside the grid. Perimeter/fence check and the final ring designs are on 'Sweep D' and 'Final Design'.

## Budget vs Benchmark
Project budget for the grounding system vs. typical budget (BDT) – FINAL DESIGN
Line item | FINAL: 6×6 + ring, 20 rods × 9 m | Alternative: 5×5 + ring, 20 rods × 9 m | Basis
Grid conductor – supply + trench/lay | 895517.9366 | 783578.1946 | Sweep D col R (grid + ring + ties)
Ground rods – sections, couplers, driving | 486000 | 486000 | Sweep sheets col S
Exothermic joints | 160000 | 130000 | Sweep D col T (grid crossings + rod welds + tie welds)
Surface layer – crushed stone supply + spreading | 903756.1451 | 903756.1451 | (side + 2×ext)² × thickness, ×35.3147 cft/m³
Soil survey & commissioning tests | 60000 | 60000 | Lump sum
Direct cost subtotal | 2505274.0817 | 2363334.3396 | Sum
Contractor overhead & profit | 250527.4082 | 236333.434 | × OH&P
Contingency | 275580.149 | 259966.7774 | × contingency
VAT | 303138.1639 | 285963.4551 | × VAT
TOTAL grounding system budget (BDT) | 3334519.8027 | 3145598.006
TOTAL (USD) | 27131.9756 | 25594.7763
TOTAL (lakh BDT) | 33.3452 | 31.456
Grid-only total incl. mark-ups & VAT (excl. surface layer) | 2131620.3737 | 1942698.577 | Crushed rock is often costed under civil/yard works – this line isolates the electrical earthing scope
BENCHMARK – typical budget
Typical 33/11 kV substation cost – low | 25000000 |  | AB Power Engineering (BD)
Typical 33/11 kV substation cost – high | 40000000 |  | AB Power Engineering (BD)
Typical earthing budget – low (low cost × low share) | 500000 |  | Rule-of-thumb share (Unit Rates)
Typical earthing budget – high (high cost × high share) | 2000000 |  | Rule-of-thumb share (Unit Rates)
Typical earthing budget – mid-point | 1250000 |  | Average of low & high
COMPARISON
Full budget vs typical mid-point | 166.8% | 151.6%
Full budget within typical range? | Above range | Above range
Grid-only vs typical mid-point | 70.53% | 55.42%
Grid-only within typical range? | Above range | Within range
Full budget as % of mid-range substation cost | 10.26% | 9.679%
Benchmark method: typical 33/11 kV substation cost (published BD range) × assumed earthing share (2–5%). No public BD average exists for a 30×30 m grid, so treat this as an order-of-magnitude check and replace with a BREB/PGCB tender BOQ if you can obtain one.
All rates are editable on 'Unit Rates'. Yellow cells are the ones most worth confirming with a local supplier quotation (copper conductor, rods, exothermic welds).